MODULE-23

SAFETY MEASURES FOR ELEVATOR SYSTEMS DURING FIRE CONDITIONS

Ensuring the safe operation of elevators during a fire is critically important for both passenger safety and the effectiveness of evacuation plans. The following measures are in line with relevant regulations and standards, especially TS EN 81-73, and outline the necessary actions during a fire event:

1. Integration with Fire/Earthquake Detection Systems

Fire detection system and earthquake sensor cables must be routed up to the elevator control panel by the building owner or elevator installer.

2. Condition for Activation of Fire Suppression Systems

Fire extinguishing systems must only be activated when the elevator is stationary at a floor, and its power and lighting have been automatically cut off by the fire or smoke detection system (both in the machine room and the shaft).

3. Elevator Movement upon Fire Alert

In high-rise and public buildings, upon receiving a fire alert, elevators with automatic doors must close their doors at the current floor and proceed directly to a predefined floor without stopping. (TS EN 81-73, Article 5.3.1)

4. “Do Not Use Elevator in Case of Fire” Sign

All landings must clearly display a prohibition sign in accordance with TS ISO 3864-1, indicating that elevators must not be used in the event of a fire. The minimum size of the sign is 50 mm, with a graphical symbol as shown in Figure 1. (TS EN 81-73, Article 5.1.3)

5. Emergency Elevator Requirements

The emergency elevator must have a cabin area of at least 1.8 m², be capable of reaching the top floor from the ground floor within 1 minute, and be connected to an emergency generator that can operate for 60 minutes after a power outage.

6. Elevator Shaft Configuration

No more than 3 elevator cabins can be installed within the same shaft. If there are 4 cabins, they must be separated into pairs by materials with 60-minute fire resistance.

7. Evacuation Signal upon Fire Alarm

In high-rise and public buildings, fire detection or manual recall systems must send a signal to the elevator control system to direct the cabin to a predetermined floor and enable passenger evacuation. (TS EN 81-73, Article 5.1.1)

8. Blocked Restart in Case of Fault

If the elevator is disabled due to a fault when a fire alert is received, the fire detection signal must not restart the elevator. (TS EN 81-73, Article 5.1.2.1)

9. Uninterrupted Emergency and Maintenance Controls

Fire detection systems must not affect emergency controls or maintenance operations. (TS EN 81-73, Article 5.1.2.2)

10. Response to Earthquake Signals

In seismic zones (1st and 2nd degree), elevators must be capable of moving to the nearest floor, opening their doors, and stopping movement after receiving an earthquake signal from the sensor connected to the elevator control panel. (Reference: Earthquake Zone Map published by AFAD)

11. Disabling All Control Buttons

Upon fire alert, all landing and cabin buttons (including the “door reopen” button) must be deactivated, and all registered calls must be cancelled. (TS EN 81-73, Article 5.3.1)

12. Manual Recall Device Requirements

The manual recall unit must:

a- Operate stably in two positions,

b- Be clearly marked to avoid misinterpretation,

c- Be appropriately labeled,

d- Be located in the building control center or designated main floor, and

e- If accessible to the public, be protected against misuse (e.g., behind a glass panel or within a secured area). (TS EN 81-73, Article 5.1.1)

13. In high-rise and public buildings, when a fire alert has been received, the elevator should automatically return to normal operation after the fire detection system is reset or when the manual recall system—designed to be reset only by authorized personnel—is reset. (TS EN 81-73, Article 5.3.7)

14.  In high-rise and public buildings, a fault in one elevator within a group of interconnected elevators must not prevent the other elevators from returning to their designated floor. (TS EN 81-73, Article 5.3.4)

15. In high-rise and public buildings, upon a fire alert, elevators with manually operated or non-automated doors must remain stationary at the landing if parked with open doors. If the doors are closed, they should proceed to the designated floor.

16.  In high-rise and public buildings, elevators that have moved away from the designated floor upon receiving a fire alert must stop normally, reverse direction without opening their doors, and proceed to the designated floor.

17  In high-rise and public buildings, elevators with automatically powered doors must, upon arrival at the designated floor, park with both cabin and landing doors open and remain out of service. (TS EN 81-73, Article 5.3.5)

18.  In high-rise and public buildings, elevators en route to the designated floor after a fire alert must proceed directly without stopping. (TS EN 81-73, Article 5.3.1)

19. In high-rise and public buildings, elevators whose movement is restricted due to the activation of safety mechanisms upon a fire alert must remain immobilized. (TS EN 81-73, Article 5.3.1)

20. In high-rise and public buildings, elevators with manually operated doors must have their door locks released upon reaching the designated floor and then remain out of service. (TS EN 81-73, Article 5.3.6)

21. In high-rise and public buildings, any door reversal devices susceptible to heat or smoke must be disabled to ensure doors remain closed.
(TS EN 81-1, Article 7.5.2.1.1.3 or TS EN 81-2, Article 7.5.2.1.1)

22. The machine room of the emergency elevator must be separate, and the elevator shaft must be pressurized. (TS EN 81-72)

23. The electrical wiring and cables of emergency elevators must be fire-resistant for at least 60 minutes, and the equipment inside the elevator shaft must be protected from water.

24. In front of emergency elevators, fire-protected lobbies must be provided on every floor with an area between 6 m² and 10 m², with no dimension smaller than 2 meters. These lobbies must also allow access to emergency stairwells.

25. In buildings where the height exceeds 51.50 meters, at least one elevator must be designated as an emergency elevator in accordance with TS EN 81-72.

26. For pedestrian overpasses constructed entirely in open areas, fire resistance requirements for the elevator shaft walls and the elevator behavior during fire conditions are excluded from the scope of periodic inspection.

CONTROLLING MEASURES FOR OPERATING ELEVATORS IN CASE OF FIRE

Ensuring the safe and controlled operation of elevators during a fire requires a comprehensive planning and inspection process. The main steps and methods applied to manage this process can be summarized as follows:

1. Integration and Design Phase

- System Integration: Elevator systems must be designed to be compatible with the building’s fire alarm system and smoke/heat detectors. During the design phase, both software and hardware must be integrated so that, upon receiving a fire signal, the elevator automatically switches to emergency evacuation mode (e.g., directing to the nearest safe floor, disabling call buttons).

- Compliance with Standards: National and international standards, such as TS EN 81-73 and the Regulation on Fire Protection of Buildings, define how elevators should behave during a fire. The requirements of these standards must be considered during both the planning and material selection stages.

2. Construction and Installation Process

- Hardware Installation: It must be ensured that elevator cabins and shafts are constructed using fire-resistant materials, and that smoke-proof doors and emergency display panels are correctly installed.

- Integration of Power and Backup Systems: Emergency generators must be connected to ensure the system remains operational for a specified duration (e.g., at least 60 minutes) in the event of a power outage.

3. Testing, Drills, and Periodic Maintenance

- Emergency Testing: Fire alarm scenarios are simulated to verify whether the elevator transitions correctly to the emergency mode, disables call buttons, and opens its doors automatically. All such functions must operate flawlessly.

- Periodic Inspections: As part of regular maintenance, control, and inspection activities, both elevator maintenance companies and relevant public authorities verify the system’s functionality and update status. These inspections cover both software updates and hardware maintenance.

4. Post-Incident Monitoring and Reporting

Alarm and Data Tracking: In the event of a real fire, elevator responses—such as automatic call cancellations and emergency mode activation—are monitored and recorded. These logs are later used for audits.

Corrective Actions: If any issues are identified, action plans are implemented to eliminate deficiencies and update the system accordingly.

This control process is rigorously conducted by building authorities, elevator maintenance companies, and government inspection agencies. Through both regulatory compliance and field tests and drills, elevators can be made safely operable and controllable during fire emergencies.

MODULE-23 APPLICATION AND OUTPUTS

CONTROLLING FIRE DETECTION SENSORS

A fire alarm system consists of the following components:

Fire Alarm Control Panel:
This is the control center of the fire alarm system. Electrical signals received from detectors are processed here and transmitted to output devices such as sirens, auto-dialers, relays, and indicator LEDs.

Detectors:
       These are sensors that detect fire elements such as heat, smoke, or flames, and transmit this information to the panel in the form of electrical signals.

Manual Call Points (Fire Buttons):
       These are buttons that can be pressed to trigger the alarm system in the early stages of a fire or when there is a suspected fire or explosion risk.

Sirens:
       Once the fire alarm panel receives a fire signal, it sends an output to the siren, which alerts people by producing a high-intensity sound.

In addition to these, the system can also include integrated fire extinguishing systems and illuminated emergency exit signs that indicate escape routes during panic situations. These are classified as auxiliary components.

Figure 23.1 Sample Fire Alarm System Equipment

The frequency of maintenance for fire detection systems is defined in regulations as at least once per year. However, maintenance intervals are also specified considering the safety of life and property at the facility.

- Daily Checks include simple inspections that business owners can perform on their own.

- Monthly Checks involve testing the backup power supply and monitoring fault indicators.

- Quarterly Checks include tasks such as regional testing, checking the system log, inspecting the control and display devices, testing control and monitoring functions, and reviewing any structural changes.

- Annual Checks, in addition to the tasks above, include battery testing, verifying device accessibility, and full-system tests to ensure all detectors are functioning properly.

Scope of Fire Alarm System Maintenance

- All components of the fire alarm system must be accessible during periodic testing and maintenance. The products in the fire alarm system to be tested can be listed as follows:

- Fire detectors

- Explosion-proof (Ex-proof) detectors

- Fire alarm panels

- Sirens

- Flashers

- Fire alarm buttons (manual call points)

- Carbon monoxide detection system

How Should Fire Detection System Maintenance Be Carried Out?

Since the fire detection system protects life and property, the experience and brand expertise of the maintenance provider is crucial. The company performing maintenance must be fully trained and certified for the specific fire alarm software and control panel brand. Many global brands provide competency certifications to their local partners and distributors.

As a building manager or owner, you should request the brand certification from the company providing maintenance. Otherwise, in case of a fire risk, the building owner may also be held accountable for assigning this critical task to unqualified individuals or companies.

Key Points to Consider During Fire Maintenance:

- All devices that make up the fire alarm system should be tested for functionality and performance.

- Devices connected to the fire alarm system should be tested to ensure they operate according to the fire scenario.

- The functionality of the control panel’s electronic boards should be verified.

- Zone-based alarms should be triggered to verify the fire scenario functionality.

- The functionality of power supply sources should be checked.

- Any devices requiring calibration should be inspected and adjusted as necessary.

- Detectors showing contamination alerts in the fire detection software should be investigated and resolved.

- Fault monitoring features of the control and display hardware should be tested.

- Battery status, voltage, and connections in the fire system should be inspected.

- Any system faults or errors should be reviewed through the software.

- Fire system software updates should be uploaded to the control panel to improve performance.

- General cleaning of detectors should be performed if needed.

KNOWING AND CONTROLLING THE OPERATING CONDITIONS OF ELEVATORS IN CASE OF FIRE ALERT

The fire detection and alarm system must be designed in accordance with the emergency control functions stated in Article 82 of the Regulation on Fire Protection of Buildings and the operating principles of other fire protection systems specified in Articles 13 and 14.2 of TS EN/TS 54-14.

Accordingly, the fire detection and alarm system to be installed in a building must be designed in such a way that its hardware and software components can fully integrate and operate in coordination with other fire protection systems specified below.

The behavior of elevators during fire and earthquake conditions is defined in the TS EN 81-73 standard. According to this standard:

In the event of a fire, elevators shall automatically proceed to the fire emergency floor (usually designated as the ground floor).

If the fire is located on the emergency floor, the elevators must proceed to a designated alternative evacuation floor.

In the event of an earthquake, elevators must stop at the nearest floor.

To enable these functions, relay control modules must be installed on the fire detection and alarm system loops that pass through elevator machine rooms.

Figure 23.2 – Elevator Control System During a Fire

In the event of a fire, relay control modules must be designed within the fire detection and alarm system to send the necessary operating commands to the elevator shafts and stairwell pressurization systems.
If motorized dampers are designed at the duct inlets of the pressurization system, then the system should first open these dampers. After receiving confirmation that the damper is open, the system must send the command to activate the pressurization fan using monitoring and control mechanisms.

Regulation on Fire Protection of Buildings

Article 62 ( 5) : Elevators in high-rise buildings and public facilities must comply with the following principles:

a) Elevators must, upon receiving a fire alarm, automatically travel to the emergency evacuation floor, regardless of their current direction, without opening the doors at other floors, and wait with doors open at the evacuation floor. Additionally, the elevators must be equipped with an electrical system that allows them to be used by authorized personnel if necessary.

b) When a fire alarm is received, elevators must ignore all hall and corridor calls.

c) In high-rise buildings located in first- and second-degree seismic zones, elevators must be equipped with a system and software that allows them to stop at the nearest floor, open the doors, and remain stationary upon receiving a signal from an earthquake sensor.

TS EN 81-73 Standard – Section 5.3: Elevator Behavior Upon Receiving a Fire Detection Signal

The general principle for elevator response during a fire is that the cabin must travel to a predetermined floor and allow passengers to exit safely.

Section 5.3.1: When a signal indicating fire is received either from the automatic fire detection and alarm system or from a manual activation device, the elevator must respond as follows:

a) All landing and cabin controls, including the “door reopen button,” must be disabled.

b) All existing registered calls must be canceled.

c) The elevator must follow automatic commands initiated by the received signal as outlined below:

1- Elevators with automatic doors powered by machine drive must close their doors (if parked at a floor) and proceed directly to the designated evacuation floor without stopping.

2- For manually operated or non-automatic machine-driven doors:

- If parked with doors open, the elevator must remain stationary.

- If doors are closed, the elevator must proceed directly to the designated floor without stopping.

3- Elevators moving away from the designated floor must stop normally, then reverse direction without opening the doors and proceed to the designated evacuation floor.

4- Elevators already moving towards the designated floor must continue without stopping until they reach that floor.

5- Elevators prevented from moving due to a safety device must remain stationary.

INSPECTION OF FIRE-RESISTANT LANDING DOORS

In Turkiye, the production of fire-resistant elevator doors is governed by the TS EN 81-58:2018 standard and the Regulation on the Protection of Buildings from Fire. The standard outlines how doors must be tested and details the procedures to be followed. Currently, there are two accredited laboratories in Turkey that perform these tests. Tests are conducted according to the relevant standard, and a report and certificate are issued based on the performance of the elevator landing door.

Generally, fire-resistant elevator landing doors are used to prevent the passage of smoke and flames. The primary expectation from these doors is that they resist the passage of fire, heat, and smoke long enough to allow the safe evacuation of building occupants.

According to EN 81-58:2018, the performance categories of such doors are:

Integrity (E): The primary criterion used in evaluating fire resistance of elevator landing doors.

Insulation (I): The door’s ability to prevent heat transfer.

Radiation (W): The door’s ability to limit heat radiation.

When designing and manufacturing fire-resistant doors, specific rules must be followed as defined by applicable standards and directives. In Turkey, these applications must comply with the Regulation on the Protection of Buildings from Fire, which was last amended on November 4, 2020.

This regulation clearly states:

“Elevator doors must be resistant to fire for at least 30 minutes and be smoke-tight; in buildings with a height over 51.5 meters, they must resist fire for at least 60 minutes and be smoke-tight.”

In addition, Annex I of Directive 2014/33/EU on lifts specifies that:

“If elevator landing doors contribute to fire protection, including those with glass components, they must be fire-resistant in terms of integrity, insulation, and heat transfer.”

Also, according to the Regulation on the Protection of Buildings from Fire, all elevator landing doors must be fire-resistant, regardless of whether they contribute directly to fire protection or not.

INSPECTION CHECKLIST FOR FIRE-RESISTANT ELEVATOR DOORS

1. Door Opening and Closing Control

- The door must open and close smoothly.

- It should operate without jamming or rubbing against surrounding surfaces.

2. Lock and Mechanism Checks

- The locking mechanism must function properly and ensure secure closure.

- The door must be manually operable in emergency situations.

3. Seal and Insulation Checks

- Seals that prevent smoke and flame penetration must be intact and undamaged.

- Worn or damaged seals must be replaced immediately.

4. Self-Closing Feature

- The automatic closing mechanism must function correctly.

- Spring hinges or hydraulic systems should be tested periodically.

5. Fire Resistance and Material Inspection

- The door must be made from fire-resistant materials.

- Compliance with fire safety standards such as TS EN 81-80 and TS EN 1634-1 must be verified.